## YBus
Bus
Number | Name | Bus 1 | Bus 2 | Bus 3 | Bus 4 | Bus 5 | Bus 6 | Bus 7 | Bus 8 | Bus 9 | Bus 10 | Bus 11 | Bus 12 | Bus 13
1 | 1_TransmissionBus | 0.31 - j2.46 | -0.15 + j1.17 | -0.15 + j1.17
2 | Left | -0.15 + j1.17 | 2.10 - j105.18 | -0.00 + j100.00 | -1.96 + j4.06
3 | Right | -0.15 + j1.17 | -0.00 + j100.00 | 0.14 - j101.12 | [5 empty] | 0.00 + j0.00
4 | 4com |  | -1.96 + j4.06 |  | 3.93 - j8.13 | -1.96 + j4.06
5 | 5ind |  |  |  | -1.96 + j4.06 | 3.93 - j8.12 | -1.96 + j4.06
6 | 6com |  |  |  |  | -1.96 + j4.06 | 3.93 - j8.13 | -1.96 + j4.06
7 | 7res | [5 empty] | -1.96 + j4.06 | 3.93 - j8.12 | -1.96 + j4.06
8 | 8ind | [6 empty] | -1.96 + j4.06 | 3.93 - j8.12 |  |  |  |  | -1.96 + j4.06
9 | 9com |  |  | 0.00 + j0.00 | [5 empty] | 0.00 + j0.00 | 0.00 + j0.00
10 | 10res | [8 empty] | 0.00 + j0.00 | 1.96 - j4.05 | -1.96 + j4.06
11 | 11res | [9 empty] | -1.96 + j4.06 | 3.93 - j8.13 | -1.96 + j4.06
12 | 12res | [10 empty] | -1.96 + j4.06 | 3.93 - j8.12 | -1.96 + j4.06
13 | 13ind | [7 empty] | -1.96 + j4.06 |  |  |  | -1.96 + j4.06 | 3.93 - j8.12

## Regulated Buses Remotely
Bus
Number | Name | Area Name | PU Volt | Set Volt | Volt Diff | AVR | Total Mvar | Mvar Min | Mvar Max | Rem Regs (gen) | Rem Regs (XFMR) | Rem Regs (SS) | Rem Regs (VSC DC) | Rem Regs (SVC) | Rem Reg Gen Bus 1
1 | 1_TransmissionBus | Residential | 1 | [6 empty] | Generator: 1 #1 |  |  |  |  | 1
5 | 5ind | Industrial | 1.0459
7 | 7res | Residential | 1.0436
8 | 8ind | Industrial | 1.0431
10 | 10res | Residential | 1.0419
12 | 12res | Residential | 1.0422
13 | 13ind | Industrial | 1.0426

## Power Flow Jacobian
Bus
Number | Name | Jacobian Equation | Angle Bus 1 | Angle Bus 2 | Angle Bus 3 | Angle Bus 4 | Angle Bus 5 | Angle Bus 6 | Angle Bus 7 | Angle Bus 8 | Angle Bus 9 | Angle Bus 10 | Angle Bus 11 | Angle Bus 12 | Angle Bus 13 | Volt Mag Bus 1 | Volt Mag Bus 2 | Volt Mag Bus 3 | Volt Mag Bus 4 | Volt Mag Bus 5 | Volt Mag Bus 6 | Volt Mag Bus 7 | Volt Mag Bus 8 | Volt Mag Bus 9 | Volt Mag Bus 10 | Volt Mag Bus 11 | Volt Mag Bus 12 | Volt Mag Bus 13
1 | 1_TransmissionBus | Real Power | 1
1 | 1_TransmissionBus | Slack | [13 empty] | 1
2 | Left | Reactive Power |  | -2.33 | 0.05 | 2.08 | [10 empty] | 110.74 | -105.29 | -4.32
2 | Left | Real Power |  | 116.6 | -110.85 | -4.53 | [10 empty] | 2.22 | -0.04 | -1.99
3 | Right | Reactive Power |  | -0.05 | -0.16 | [11 empty] | -105.28 | 106.46
3 | Right | Real Power |  | -110.85 | 112.08 | [11 empty] | 0.04 | 0.15
4 | 4com | Reactive Power |  | 2.25 |  | -4.33 | 2.08 | [9 empty] | -4.22 |  | 8.52 | -4.3
4 | 4com | Real Power |  | -4.44 |  | 8.94 | -4.49 | [9 empty] | -2.14 |  | 4.11 | -1.99
5 | 5ind | Reactive Power |  |  |  | 2.23 | -4.31 | 2.08 | [10 empty] | -4.21 | 8.48 | -4.28
5 | 5ind | Real Power |  |  |  | -4.42 | 8.89 | -4.47 | [10 empty] | -2.13 | 4.1 | -1.99
6 | 6com | Reactive Power |  |  |  |  | 2.21 | -4.29 | 2.08 | [10 empty] | -4.21 | 8.48 | -4.27
6 | 6com | Real Power |  |  |  |  | -4.4 | 8.86 | -4.46 | [10 empty] | -2.11 | 4.09 | -1.99
7 | 7res | Reactive Power | [5 empty] | 2.2 | -4.29 | 2.09 | [10 empty] | -4.21 | 8.47 | -4.26
7 | 7res | Real Power | [5 empty] | -4.4 | 8.84 | -4.45 | [10 empty] | -2.11 | 4.09 | -2
8 | 8ind | Reactive Power | [6 empty] | 2.19 | -4.28 |  |  |  |  | 2.1 | [6 empty] | -4.22 | 8.46 |  |  |  |  | -4.26
8 | 8ind | Real Power | [6 empty] | -4.4 | 8.84 |  |  |  |  | -4.44 | [6 empty] | -2.1 | 4.09 |  |  |  |  | -2.01
9 | 9com | Reactive Power | [21 empty] | 1
9 | 9com | Real Power | [8 empty] | 1
10 | 10res | Reactive Power | [9 empty] | -2.14 | 2.14 | [11 empty] | 4.22 | -4.23
10 | 10res | Real Power | [9 empty] | 4.4 | -4.4 | [11 empty] | 2.04 | -2.06
11 | 11res | Reactive Power | [9 empty] | 2.12 | -4.27 | 2.15 | [10 empty] | -4.24 | 8.46 | -4.22
11 | 11res | Real Power | [9 empty] | -4.41 | 8.82 | -4.4 | [10 empty] | -2.03 | 4.08 | -2.06
12 | 12res | Reactive Power | [10 empty] | 2.11 | -4.28 | 2.16 | [10 empty] | -4.24 | 8.46 | -4.22
12 | 12res | Real Power | [10 empty] | -4.42 | 8.82 | -4.4 | [10 empty] | -2.03 | 4.08 | -2.07
13 | 13ind | Reactive Power | [7 empty] | 2.17 |  |  |  | 2.1 | -4.28 | [7 empty] | -4.22 |  |  |  | -4.25 | 8.46
13 | 13ind | Real Power | [7 empty] | -4.4 |  |  |  | -4.43 | 8.83 | [7 empty] | -2.08 |  |  |  | -2.02 | 4.09

## Solution Details - Mismatches
Bus
Number | Name | Area Name | Type | Mismatch MW | Mismatch Mvar | Mismatch MVA
10 | 10res | Residential | PQ | 0 | 0 | 0
11 | 11res | Residential | PQ | 0 | 0 | 0
12 | 12res | Residential | PQ | 0 | 0 | 0
13 | 13ind | Industrial | PQ | 0 | 0 | 0
8 | 8ind | Industrial | PQ | 0 | 0 | 0
7 | 7res | Residential | PQ | 0 | 0 | 0
6 | 6com | Commercial | PQ | 0 | 0 | 0
5 | 5ind | Industrial | PQ | 0 | 0 | 0
4 | 4com | Commercial | PQ | 0 | 0 | 0
3 | Right | Residential | PQ | 0 | 0 | 0
2 | Left | Residential | PQ | 0 | 0 | 0
9 | 9com | Commercial | Dead | 0 | 0 | 0
1 | 1_TransmissionBus | Residential | Slack | 0 | 0 | 0

## FD BPP Matrix
Bus
Number | Name | Jacobian Equation | Volt Mag Bus 1 | Volt Mag Bus 2 | Volt Mag Bus 3 | Volt Mag Bus 4 | Volt Mag Bus 5 | Volt Mag Bus 6 | Volt Mag Bus 7 | Volt Mag Bus 8 | Volt Mag Bus 9 | Volt Mag Bus 10 | Volt Mag Bus 11 | Volt Mag Bus 12 | Volt Mag Bus 13
1 | 1_TransmissionBus | Slack | 1
2 | Left | Reactive Power |  | -105.18 | 100 | 4.06
3 | Right | Reactive Power |  | 100 | -101.12
4 | 4com | Reactive Power |  | 4.06 |  | -8.13 | 4.06
5 | 5ind | Reactive Power |  |  |  | 4.06 | -8.12 | 4.06
6 | 6com | Reactive Power |  |  |  |  | 4.06 | -8.13 | 4.06
7 | 7res | Reactive Power | [5 empty] | 4.06 | -8.12 | 4.06
8 | 8ind | Reactive Power | [6 empty] | 4.06 | -8.12 |  |  |  |  | 4.06
9 | 9com | Reactive Power | [8 empty] | 1
10 | 10res | Reactive Power | [9 empty] | -4.05 | 4.06
11 | 11res | Reactive Power | [9 empty] | 4.06 | -8.13 | 4.06
12 | 12res | Reactive Power | [10 empty] | 4.06 | -8.12 | 4.06
13 | 13ind | Reactive Power | [7 empty] | 4.06 |  |  |  | 4.06 | -8.12

## FD BP Matrix
Bus
Number | Name | Jacobian Equation | Angle Bus 1 | Angle Bus 2 | Angle Bus 3 | Angle Bus 4 | Angle Bus 5 | Angle Bus 6 | Angle Bus 7 | Angle Bus 8 | Angle Bus 9 | Angle Bus 10 | Angle Bus 11 | Angle Bus 12 | Angle Bus 13
1 | 1_TransmissionBus | Real Power | 1
2 | Left | Real Power |  | -106.26 | 100 | 5.01
3 | Right | Real Power |  | 100 | -101.25
4 | 4com | Real Power |  | 5.01 |  | -10.03 | 5.01
5 | 5ind | Real Power |  |  |  | 5.01 | -10.03 | 5.01
6 | 6com | Real Power |  |  |  |  | 5.01 | -10.03 | 5.01
7 | 7res | Real Power | [5 empty] | 5.01 | -10.03 | 5.01
8 | 8ind | Real Power | [6 empty] | 5.01 | -10.03 |  |  |  |  | 5.01
9 | 9com | Real Power | [8 empty] | 1
10 | 10res | Real Power | [9 empty] | -5.01 | 5.01
11 | 11res | Real Power | [9 empty] | 5.01 | -10.03 | 5.01
12 | 12res | Real Power | [10 empty] | 5.01 | -10.03 | 5.01
13 | 13ind | Real Power | [7 empty] | 5.01 |  |  |  | 5.01 | -10.03

## Bus Zero-Impedance Branch Group
Bus
Number | Name | Area Name | Nom kV | ZBR Bus Primary | ZBR Bus Neighbor List
1 | 1_TransmissionBus | Residential | 138 | 1
2 | Left | Residential | 13.8 | 2
3 | Right | Residential | 13.8 | 3
4 | 4com | Commercial | 13.8 | 4
5 | 5ind | Industrial | 13.8 | 5
6 | 6com | Commercial | 13.8 | 6
7 | 7res | Residential | 13.8 | 7
8 | 8ind | Industrial | 13.8 | 8
9 | 9com | Commercial | 13.8 | 9
10 | 10res | Residential | 13.8 | 10
11 | 11res | Residential | 13.8 | 11
12 | 12res | Residential | 13.8 | 12
13 | 13ind | Industrial | 13.8 | 13

## Zones
Zone
Zone Num | Zone Name | Load MW | Load Mvar | Gen MW | Gen Mvar | Dist MW | Loss MW | Loss Mvar | Int MW | Int Mvar | Load Mult MW
1 | Residential | 9 | 3.9 | 9.34 | -1.67 | 0 | 0.3363 | 0.9646 | 0 | 0 | 1

## Owners
Owner
Owner Number | Owner Name | Num Buses | Num Loads | Num Gens | Min Bus Num | Max Bus Num | Gen MW | Gen Mvar | Gen Max MW | Load MW | Load Mvar | Num Devices | Num Branches | Memo
1 | 1 | 13 | 10 | 1 | 1 | 13 | 9.34 | -1.67 | 1000 | 9 | 3.9 | 44 | 14

## Islands
Island
Number | Slack Bus Number | Slack Bus Name | Slack Bus Area Name | # of Buses | Solved | Energized | Gen MW | Gen Mvar | Load MW | Load Mvar | Scheduled Exports | DC MW Exports
1 | 1 | 1_TransmissionBus | Residential | 12 | YES | YES | 9.3 | -1.7 | 9 | 3.9 | 0 | 0

## Case Summary
PWCaseInformation
Gen MW | Gen Mvar | Load MW | Load Mvar | Dist MW | Dist Mvar | Shunts Actual Mvar | Shunts Actual MW | Losses Mvar | Losses MW | # of Buses | # of Loads | # of Gens | # of Switched Shunts | # of AC Lines | # of Series Caps | # of LTCs | # of LTCs (Mvar) | # of Phase Shifters
9.3 | -1.6 | 9 | 3.9 | 0 | 0 | -6.5 | 0 | 0.9646 | 0.3363 | 13 | 10 | 1 | 6 | 12 | 0 | 2 | 0 | 0

## Areas
Area
Area Num | Area Name | AGC Status | Gen MW | Load MW | Shunt MW | Dist MW | Tot Sched MW | Int MW | ACE MW | Lambda | Loss MW | Auto Shunts | Auto XF | Area Slack Bus | Unspec. MW Inter. | AGC Tolerance
1 | Residential | Off AGC | 9.34 | 4 | 0 | 0 | 0 | 5.24 | 5.24 | Off Control | 0.1 | YES | YES |  | 0 | 1
2 | Commercial | Off AGC |  | 2 |  | 0 | 0 | -2.13 | -2.13 | Off Control | 0.13 | YES | YES |  | 0 | 1
3 | Industrial | Off AGC |  | 3 | 0 | 0 | 0 | -3.11 | -3.11 | Off Control | 0.11 | YES | YES |  | 0 | 1

## Transformer Controls
Branch
From Number | From Name | To Number | To Name | Circuit | Type | Status | Tap Ratio | Phase (Deg) | Automatic Control | Reg Bus Num | Reg Value | Reg Error | Reg Min | Reg Max | Tap Min | Tap Max | Step Size | Reg Bus Name
2 | Left | 1 | 1_TransmissionBus | 1 | LTC | Closed | 1.05 | 0 | NO | 1 | 1 | 0 | 0.99 | 1.01 | 0.9 | 1.1 | 0.00625 | 1_TransmissionBus
3 | Right | 1 | 1_TransmissionBus | 1 | LTC | Closed | 1.05 | 0 | NO | 1 | 1 | 0 | 0.99 | 1.01 | 0.9 | 1.1 | 0.00625 | 1_TransmissionBus

## Switched Shunts
Shunt
Number of Bus | Name of Bus | ID | Reg Bus Num | Status | Status Branch | Control Mode | Auto Control | Regulates | Actual Mvar | Volt High | Volt Low | Reg Volt | Deviation | Nominal Mvar | Max Mvar | Min Mvar | Range Mvar | Percent Mvar
5 | 5ind | 1 | 5 | Closed |  | Fixed | YES | Volt | 1.09 | 1 | 0.99 | 1.046 | 0.046 | 1 | 1 | 0 | 1 | 100
7 | 7res | 1 | 7 | Closed |  | Fixed | YES | Volt | 1.09 | 1 | 0.99 | 1.0436 | 0.0436 | 1 | 1 | 0 | 1 | 100
8 | 8ind | 1 | 8 | Closed |  | Fixed | YES | Volt | 1.09 | 1 | 0.99 | 1.0431 | 0.0431 | 1 | 1 | 0 | 1 | 100
10 | 10res | 1 | 10 | Closed |  | Fixed | YES | Volt | 1.09 | 1 | 0.99 | 1.0419 | 0.0419 | 1 | 1 | 0 | 1 | 100
12 | 12res | 1 | 12 | Closed |  | Fixed | YES | Volt | 1.09 | 1 | 0.99 | 1.0422 | 0.0422 | 1 | 1 | 0 | 1 | 100
13 | 13ind | 1 | 13 | Closed |  | Fixed | YES | Volt | 1.09 | 1 | 0.99 | 1.0426 | 0.0426 | 1 | 1 | 0 | 1 | 100

## Mismatches
Bus
Number | Name | Area Name | Type | Mismatch MW | Mismatch Mvar | Mismatch MVA
10 | 10res | Residential | PQ | 0 | 0 | 0
11 | 11res | Residential | PQ | 0 | 0 | 0
12 | 12res | Residential | PQ | 0 | 0 | 0
13 | 13ind | Industrial | PQ | 0 | 0 | 0
8 | 8ind | Industrial | PQ | 0 | 0 | 0
7 | 7res | Residential | PQ | 0 | 0 | 0
6 | 6com | Commercial | PQ | 0 | 0 | 0
5 | 5ind | Industrial | PQ | 0 | 0 | 0
4 | 4com | Commercial | PQ | 0 | 0 | 0
3 | Right | Residential | PQ | 0 | 0 | 0
2 | Left | Residential | PQ | 0 | 0 | 0
9 | 9com | Commercial | Dead | 0 | 0 | 0
1 | 1_TransmissionBus | Residential | Slack | 0 | 0 | 0

## Loads
Load
Number of Bus | Name of Bus | Area Name of Load | Zone Name of Load | ID | Status | MW | Mvar | MVA | S MW | S Mvar | Dist Status | Dist MW Input | Dist Mvar Input
4 | 4com | Commercial | Residential | 1 | Closed | 1 | 0.4 | 1.08 | 1 | 0.4 | Closed | 0 | 0
5 | 5ind | Industrial | Residential | 1 | Closed | 1 | 0.6 | 1.17 | 1 | 0.6 | Closed | 0 | 0
6 | 6com | Commercial | Residential | 1 | Closed | 1 | 0.5 | 1.12 | 1 | 0.5 | Closed | 0 | 0
7 | 7res | Residential | Residential | 1 | Closed | 1 | 0.3 | 1.04 | 1 | 0.3 | Closed | 0 | 0
8 | 8ind | Industrial | Residential | 1 | Closed | 1 | 0.6 | 1.17 | 1 | 0.6 | Closed | 0 | 0
9 | 9com | Commercial | Residential | 1 | Closed | 0 | 0 | 0 | 1 | 0.5 | Closed | 0 | 0
10 | 10res | Residential | Residential | 1 | Closed | 1 | 0.3 | 1.04 | 1 | 0.3 | Closed | 0 | 0
11 | 11res | Residential | Residential | 1 | Closed | 1 | 0.3 | 1.04 | 1 | 0.3 | Closed | 0 | 0
12 | 12res | Residential | Residential | 1 | Closed | 1 | 0.3 | 1.04 | 1 | 0.3 | Closed | 0 | 0
13 | 13ind | Industrial | Residential | 1 | Closed | 1 | 0.6 | 1.17 | 1 | 0.6 | Closed | 0 | 0

## Generators
Gen
Number of Bus | Name of Bus | ID | Status | Gen MW | Gen Mvar | Min MW | Max MW | AGC | AVR | RegBus Num | Set Volt | Min Mvar | Max Mvar | Enforce MW Limits | Part. Factor | Cost Model
1 | 1_TransmissionBus | 1 | Closed | 9.34 | -1.67 | 0 | 1000 | YES | YES | 1 | 1 | -9900 | 9900 | YES | 10 | Cubic

## Buses
Bus
Number | Name | Area Name | Nom kV | PU Volt | Volt (kV) | Angle (Deg) | Gen MW | Gen Mvar | Load MW | Load Mvar | Dist MW | Dist Mvar | Switched Shunts Mvar | Act G Shunt MW | Act B Shunt Mvar | Area Num | Zone Num
1 | 1_TransmissionBus | Residential | 138 | 1 | 138 | 0 | 9.34 | -1.67 | [5 empty] | 0 | 0 | 1 | 1
2 | Left | Residential | 13.8 | 1.0529 | 14.53 | -2.19 | [7 empty] | 0 | 0 | 1 | 1
3 | Right | Residential | 13.8 | 1.0528 | 14.529 | -2.17 | [7 empty] | 0 | 0 | 1 | 1
4 | 4com | Commercial | 13.8 | 1.0484 | 14.468 | -3.26 |  |  | 1 | 0.4 | 0 | 0 |  | 0 | 0 | 2 | 1
5 | 5ind | Industrial | 13.8 | 1.0459 | 14.434 | -4.24 |  |  | 1 | 0.6 | 0 | 0 | 1.09 | 0 | 0 | 3 | 1
6 | 6com | Commercial | 13.8 | 1.0437 | 14.404 | -5.11 |  |  | 1 | 0.5 | 0 | 0 |  | 0 | 0 | 2 | 1
7 | 7res | Residential | 13.8 | 1.0436 | 14.402 | -5.89 |  |  | 1 | 0.3 | 0 | 0 | 1.09 | 0 | 0 | 1 | 1
8 | 8ind | Industrial | 13.8 | 1.0431 | 14.394 | -6.53 |  |  | 1 | 0.6 | 0 | 0 | 1.09 | 0 | 0 | 3 | 1
9 | 9com | Commercial | 13.8 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 2 | 1
10 | 10res | Residential | 13.8 | 1.0419 | 14.378 | -7.8 |  |  | 1 | 0.3 | 0 | 0 | 1.09 | 0 | 0 | 1 | 1
11 | 11res | Residential | 13.8 | 1.0413 | 14.37 | -7.65 |  |  | 1 | 0.3 | 0 | 0 |  | 0 | 0 | 1 | 1
12 | 12res | Residential | 13.8 | 1.0422 | 14.383 | -7.42 |  |  | 1 | 0.3 | 0 | 0 | 1.09 | 0 | 0 | 1 | 1
13 | 13ind | Industrial | 13.8 | 1.0426 | 14.388 | -7.04 |  |  | 1 | 0.6 | 0 | 0 | 1.09 | 0 | 0 | 3 | 1

## Branches - State
Branch
From Number | From Name | To Number | To Name | Circuit | Status | Branch Device Type | Xfrmr | MW From | Mvar From | MVA From | Lim MVA | % of MVA Limit (Max) | MW Loss | Mvar Loss
2 | Left | 1 | 1_TransmissionBus | 1 | Closed | Transformer | YES | -4.7 | 1 | 4.8 | 12 | 39.8 | 0.02 | 0.18
2 | Left | 3 | Right | 1 | Closed | Line | NO | -4.6 | 1 | 4.7 | 50 | 9.5 | 0 | 0
2 | Left | 4 | 4com | 1 | Closed | Line | NO | 9.3 | -2 | 9.5 | 12.7 | 74.9 | 0.08 | 0.16
3 | Right | 1 | 1_TransmissionBus | 1 | Closed | Transformer | YES | -4.6 | 1 | 4.7 | 12 | 39.4 | 0.02 | 0.18
3 | Right | 9 | 9com | 1 | Open | Line | NO | 0 | 0 | 0 | 12.7 | 0 | 0 | 0
4 | 4com | 5 | 5ind | 1 | Closed | Line | NO | 8.2 | -2.6 | 8.6 | 12.7 | 67.8 | 0.07 | 0.13
5 | 5ind | 6 | 6com | 1 | Closed | Line | NO | 7.1 | -2.2 | 7.5 | 12.7 | 59 | 0.05 | 0.1
6 | 6com | 7 | 7res | 1 | Closed | Line | NO | 6.1 | -2.8 | 6.7 | 12.7 | 52.9 | 0.04 | 0.08
7 | 7res | 8 | 8ind | 1 | Closed | Line | NO | 5.1 | -2.1 | 5.5 | 12.7 | 43.2 | 0.03 | 0.06
8 | 8ind | 13 | 13ind | 1 | Closed | Line | NO | 4 | -1.7 | 4.4 | 12.7 | 34.4 | 0.02 | 0.04
9 | 9com | 10 | 10res | 1 | Open | Line | NO | 0 | 0 | 0 | 12.7 | 0 | 0 | 0
10 | 10res | 11 | 11res | 1 | Closed | Line | NO | -1 | 0.8 | 1.3 | 12.7 | 10 | 0 | 0
11 | 11res | 12 | 12res | 1 | Closed | Line | NO | -2 | 0.5 | 2.1 | 12.7 | 16.2 | 0 | 0.01
13 | 13ind | 12 | 12res | 1 | Closed | Line | NO | 3 | -1.2 | 3.3 | 12.7 | 25.7 | 0.01 | 0.02

## Branches - Input
Branch
From Number | From Name | To Number | To Name | Circuit | Status | Branch Device Type | Xfrmr | R | X | B | Lim MVA A | Lim MVA B | Lim MVA C
2 | Left | 1 | 1_TransmissionBus | 1 | Closed | Transformer | YES | 0.1 | 0.8 | 0 | 12 | 12 | 12
2 | Left | 3 | Right | 1 | Closed | Line | NO | 0 | 0.01 | 0 | 50 | 0 | 0
2 | Left | 4 | 4com | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
3 | Right | 1 | 1_TransmissionBus | 1 | Closed | Transformer | YES | 0.1 | 0.8 | 0 | 12 | 12 | 12
3 | Right | 9 | 9com | 1 | Open | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
4 | 4com | 5 | 5ind | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
5 | 5ind | 6 | 6com | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
6 | 6com | 7 | 7res | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
7 | 7res | 8 | 8ind | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
8 | 8ind | 13 | 13ind | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
9 | 9com | 10 | 10res | 1 | Open | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
10 | 10res | 11 | 11res | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
11 | 11res | 12 | 12res | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
13 | 13ind | 12 | 12res | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7