## YBus
Bus
Number | Name | Bus 1 | Bus 2 | Bus 3 | Bus 4 | Bus 5 | Bus 6 | Bus 7 | Bus 8 | Bus 9 | Bus 10 | Bus 11 | Bus 12 | Bus 13
1 | 1_TransmissionBus | 0.31 - j2.46 | -0.15 + j1.17 | -0.15 + j1.17
2 | Left | -0.15 + j1.17 | 2.10 - j105.18 | -0.00 + j100.00 | -1.96 + j4.06
3 | Right | -0.15 + j1.17 | -0.00 + j100.00 | 2.10 - j105.18 | [5 empty] | -1.96 + j4.06
4 | 4com |  | -1.96 + j4.06 |  | 3.93 - j8.13 | -1.96 + j4.06
5 | 5ind |  |  |  | -1.96 + j4.06 | 3.93 - j8.12 | -1.96 + j4.06
6 | 6com |  |  |  |  | -1.96 + j4.06 | 3.93 - j8.13 | -1.96 + j4.06
7 | 7res | [5 empty] | -1.96 + j4.06 | 3.93 - j8.12 | -1.96 + j4.06
8 | 8ind | [6 empty] | -1.96 + j4.06 | 3.93 - j8.12 |  |  |  |  | -1.96 + j4.06
9 | 9com |  |  | -1.96 + j4.06 | [5 empty] | 3.93 - j8.13 | -1.96 + j4.06
10 | 10res | [8 empty] | -1.96 + j4.06 | 3.93 - j8.12 | -1.96 + j4.06
11 | 11res | [9 empty] | -1.96 + j4.06 | 3.93 - j8.13 | -1.96 + j4.06
12 | 12res | [10 empty] | -1.96 + j4.06 | 3.93 - j8.12 | -1.96 + j4.06
13 | 13ind | [7 empty] | -1.96 + j4.06 |  |  |  | -1.96 + j4.06 | 3.93 - j8.12

## Regulated Buses Remotely
Bus
Number | Name | Area Name | PU Volt | Set Volt | Volt Diff | AVR | Total Mvar | Mvar Min | Mvar Max | Rem Regs (gen) | Rem Regs (XFMR) | Rem Regs (SS) | Rem Regs (VSC DC) | Rem Regs (SVC) | Rem Reg Gen Bus 1
1 | 1_TransmissionBus | Residential | 1 | [6 empty] | Generator: 1 #1 |  |  |  |  | 1
5 | 5ind | Industrial | 1.048
7 | 7res | Residential | 1.0477
8 | 8ind | Industrial | 1.0479
10 | 10res | Residential | 1.049
12 | 12res | Residential | 1.0483
13 | 13ind | Industrial | 1.0481

## Power Flow Jacobian
Bus
Number | Name | Jacobian Equation | Angle Bus 1 | Angle Bus 2 | Angle Bus 3 | Angle Bus 4 | Angle Bus 5 | Angle Bus 6 | Angle Bus 7 | Angle Bus 8 | Angle Bus 9 | Angle Bus 10 | Angle Bus 11 | Angle Bus 12 | Angle Bus 13 | Volt Mag Bus 1 | Volt Mag Bus 2 | Volt Mag Bus 3 | Volt Mag Bus 4 | Volt Mag Bus 5 | Volt Mag Bus 6 | Volt Mag Bus 7 | Volt Mag Bus 8 | Volt Mag Bus 9 | Volt Mag Bus 10 | Volt Mag Bus 11 | Volt Mag Bus 12 | Volt Mag Bus 13
1 | 1_TransmissionBus | Real Power | 1
1 | 1_TransmissionBus | Slack | [13 empty] | 1
2 | Left | Reactive Power |  | -2.33 | 0 | 2.12 | [10 empty] | 110.66 | -105.21 | -4.3
2 | Left | Real Power |  | 116.42 | -110.68 | -4.51 | [10 empty] | 2.21 | 0 | -2.02
3 | Right | Reactive Power |  | 0 | -2.33 | [5 empty] | 2.12 | [5 empty] | -105.21 | 110.66 | [5 empty] | -4.3
3 | Right | Real Power |  | -110.68 | 116.42 | [5 empty] | -4.51 | [5 empty] | 0 | 2.21 | [5 empty] | -2.02
4 | 4com | Reactive Power |  | 2.21 |  | -4.33 | 2.12 | [9 empty] | -4.24 |  | 8.52 | -4.28
4 | 4com | Real Power |  | -4.46 |  | 8.95 | -4.49 | [9 empty] | -2.1 |  | 4.11 | -2.02
5 | 5ind | Reactive Power |  |  |  | 2.2 | -4.32 | 2.13 | [10 empty] | -4.24 | 8.5 | -4.27
5 | 5ind | Real Power |  |  |  | -4.45 | 8.92 | -4.47 | [10 empty] | -2.09 | 4.11 | -2.03
6 | 6com | Reactive Power |  |  |  |  | 2.18 | -4.31 | 2.13 | [10 empty] | -4.24 | 8.5 | -4.26
6 | 6com | Real Power |  |  |  |  | -4.45 | 8.91 | -4.47 | [10 empty] | -2.08 | 4.1 | -2.04
7 | 7res | Reactive Power | [5 empty] | 2.18 | -4.32 | 2.15 | [10 empty] | -4.25 | 8.5 | -4.26
7 | 7res | Real Power | [5 empty] | -4.45 | 8.91 | -4.47 | [10 empty] | -2.08 | 4.11 | -2.05
8 | 8ind | Reactive Power | [6 empty] | 2.17 | -4.32 |  |  |  |  | 2.16 | [6 empty] | -4.25 | 8.5 |  |  |  |  | -4.26
8 | 8ind | Real Power | [6 empty] | -4.46 | 8.92 |  |  |  |  | -4.46 | [6 empty] | -2.07 | 4.11 |  |  |  |  | -2.06
9 | 9com | Reactive Power |  |  | 2.21 | [5 empty] | -4.34 | 2.12 | [5 empty] | -4.24 | [5 empty] | 8.53 | -4.28
9 | 9com | Real Power |  |  | -4.46 | [5 empty] | 8.96 | -4.49 | [5 empty] | -2.1 | [5 empty] | 4.11 | -2.02
10 | 10res | Reactive Power | [8 empty] | 2.2 | -4.33 | 2.13 | [10 empty] | -4.24 | 8.51 | -4.28
10 | 10res | Real Power | [8 empty] | -4.45 | 8.94 | -4.48 | [10 empty] | -2.1 | 4.11 | -2.03
11 | 11res | Reactive Power | [9 empty] | 2.19 | -4.32 | 2.14 | [10 empty] | -4.25 | 8.51 | -4.27
11 | 11res | Real Power | [9 empty] | -4.45 | 8.93 | -4.47 | [10 empty] | -2.08 | 4.11 | -2.04
12 | 12res | Reactive Power | [10 empty] | 2.18 | -4.33 | 2.15 | [10 empty] | -4.25 | 8.51 | -4.26
12 | 12res | Real Power | [10 empty] | -4.45 | 8.92 | -4.47 | [10 empty] | -2.08 | 4.11 | -2.05
13 | 13ind | Reactive Power | [7 empty] | 2.16 |  |  |  | 2.17 | -4.32 | [7 empty] | -4.26 |  |  |  | -4.25 | 8.5
13 | 13ind | Real Power | [7 empty] | -4.46 |  |  |  | -4.46 | 8.92 | [7 empty] | -2.06 |  |  |  | -2.07 | 4.11

## Solution Details - Mismatches
Bus
Number | Name | Area Name | Type | Mismatch MW | Mismatch Mvar | Mismatch MVA
9 | 9com | Commercial | PQ | 0 | 0 | 0
3 | Right | Residential | PQ | 0 | 0 | 0
13 | 13ind | Industrial | PQ | 0 | 0 | 0
10 | 10res | Residential | PQ | 0 | 0 | 0
11 | 11res | Residential | PQ | 0 | 0 | 0
8 | 8ind | Industrial | PQ | 0 | 0 | 0
12 | 12res | Residential | PQ | 0 | 0 | 0
6 | 6com | Commercial | PQ | 0 | 0 | 0
7 | 7res | Residential | PQ | 0 | 0 | 0
5 | 5ind | Industrial | PQ | 0 | 0 | 0
4 | 4com | Commercial | PQ | 0 | 0 | 0
2 | Left | Residential | PQ | 0 | 0 | 0
1 | 1_TransmissionBus | Residential | Slack | 0 | 0 | 0

## FD BPP Matrix
Bus
Number | Name | Jacobian Equation | Volt Mag Bus 1 | Volt Mag Bus 2 | Volt Mag Bus 3 | Volt Mag Bus 4 | Volt Mag Bus 5 | Volt Mag Bus 6 | Volt Mag Bus 7 | Volt Mag Bus 8 | Volt Mag Bus 9 | Volt Mag Bus 10 | Volt Mag Bus 11 | Volt Mag Bus 12 | Volt Mag Bus 13
1 | 1_TransmissionBus | Slack | 1
2 | Left | Reactive Power |  | -105.18 | 100 | 4.06
3 | Right | Reactive Power |  | 100 | -105.18 | [5 empty] | 4.06
4 | 4com | Reactive Power |  | 4.06 |  | -8.13 | 4.06
5 | 5ind | Reactive Power |  |  |  | 4.06 | -8.12 | 4.06
6 | 6com | Reactive Power |  |  |  |  | 4.06 | -8.13 | 4.06
7 | 7res | Reactive Power | [5 empty] | 4.06 | -8.12 | 4.06
8 | 8ind | Reactive Power | [6 empty] | 4.06 | -8.12 |  |  |  |  | 4.06
9 | 9com | Reactive Power |  |  | 4.06 | [5 empty] | -8.13 | 4.06
10 | 10res | Reactive Power | [8 empty] | 4.06 | -8.12 | 4.06
11 | 11res | Reactive Power | [9 empty] | 4.06 | -8.13 | 4.06
12 | 12res | Reactive Power | [10 empty] | 4.06 | -8.12 | 4.06
13 | 13ind | Reactive Power | [7 empty] | 4.06 |  |  |  | 4.06 | -8.12

## FD BP Matrix
Bus
Number | Name | Jacobian Equation | Angle Bus 1 | Angle Bus 2 | Angle Bus 3 | Angle Bus 4 | Angle Bus 5 | Angle Bus 6 | Angle Bus 7 | Angle Bus 8 | Angle Bus 9 | Angle Bus 10 | Angle Bus 11 | Angle Bus 12 | Angle Bus 13
1 | 1_TransmissionBus | Real Power | 1
2 | Left | Real Power |  | -106.26 | 100 | 5.01
3 | Right | Real Power |  | 100 | -106.26 | [5 empty] | 5.01
4 | 4com | Real Power |  | 5.01 |  | -10.03 | 5.01
5 | 5ind | Real Power |  |  |  | 5.01 | -10.03 | 5.01
6 | 6com | Real Power |  |  |  |  | 5.01 | -10.03 | 5.01
7 | 7res | Real Power | [5 empty] | 5.01 | -10.03 | 5.01
8 | 8ind | Real Power | [6 empty] | 5.01 | -10.03 |  |  |  |  | 5.01
9 | 9com | Real Power |  |  | 5.01 | [5 empty] | -10.03 | 5.01
10 | 10res | Real Power | [8 empty] | 5.01 | -10.03 | 5.01
11 | 11res | Real Power | [9 empty] | 5.01 | -10.03 | 5.01
12 | 12res | Real Power | [10 empty] | 5.01 | -10.03 | 5.01
13 | 13ind | Real Power | [7 empty] | 5.01 |  |  |  | 5.01 | -10.03

## Bus Zero-Impedance Branch Group
Bus
Number | Name | Area Name | Nom kV | ZBR Bus Primary | ZBR Bus Neighbor List
1 | 1_TransmissionBus | Residential | 138 | 1
2 | Left | Residential | 13.8 | 2
3 | Right | Residential | 13.8 | 3
4 | 4com | Commercial | 13.8 | 4
5 | 5ind | Industrial | 13.8 | 5
6 | 6com | Commercial | 13.8 | 6
7 | 7res | Residential | 13.8 | 7
8 | 8ind | Industrial | 13.8 | 8
9 | 9com | Commercial | 13.8 | 9
10 | 10res | Residential | 13.8 | 10
11 | 11res | Residential | 13.8 | 11
12 | 12res | Residential | 13.8 | 12
13 | 13ind | Industrial | 13.8 | 13

## Zones
Zone
Zone Num | Zone Name | Load MW | Load Mvar | Gen MW | Gen Mvar | Dist MW | Loss MW | Loss Mvar | Int MW | Int Mvar | Load Mult MW
1 | Residential | 10 | 4.4 | 10.16 | -1.55 | 0 | 0.16 | 0.65 | 0 | 0 | 1

## Owners
Owner
Owner Number | Owner Name | Num Buses | Num Loads | Num Gens | Min Bus Num | Max Bus Num | Gen MW | Gen Mvar | Gen Max MW | Load MW | Load Mvar | Num Devices | Num Branches | Memo
1 | 1 | 13 | 10 | 1 | 1 | 13 | 10.16 | -1.55 | 1000 | 10 | 4.4 | 44 | 14

## Islands
Island
Number | Slack Bus Number | Slack Bus Name | Slack Bus Area Name | # of Buses | Solved | Energized | Gen MW | Gen Mvar | Load MW | Load Mvar | Scheduled Exports | DC MW Exports
1 | 1 | 1_TransmissionBus | Residential | 13 | YES | YES | 10.2 | -1.5 | 10 | 4.4 | 0 | 0

## Case Summary
PWCaseInformation
Gen MW | Gen Mvar | Load MW | Load Mvar | Dist MW | Dist Mvar | Shunts Actual Mvar | Shunts Actual MW | Losses Mvar | Losses MW | # of Buses | # of Loads | # of Gens | # of Switched Shunts | # of AC Lines | # of Series Caps | # of LTCs | # of LTCs (Mvar) | # of Phase Shifters
10.1 | -1.5 | 10 | 4.4 | 0 | 0 | -6.5 | 0 | 0.646 | 0.1608 | 13 | 10 | 1 | 6 | 12 | 0 | 2 | 0 | 0

## Areas
Area
Area Num | Area Name | AGC Status | Gen MW | Load MW | Shunt MW | Dist MW | Tot Sched MW | Int MW | ACE MW | Lambda | Loss MW | Auto Shunts | Auto XF | Area Slack Bus | Unspec. MW Inter. | AGC Tolerance
1 | Residential | Off AGC | 10.16 | 4 | 0 | 0 | 0 | 6.07 | 6.07 | Off Control | 0.09 | YES | YES |  | 0 | 1
2 | Commercial | Off AGC |  | 3 |  | 0 | 0 | -3.05 | -3.05 | Off Control | 0.05 | YES | YES |  | 0 | 1
3 | Industrial | Off AGC |  | 3 | 0 | 0 | 0 | -3.02 | -3.02 | Off Control | 0.02 | YES | YES |  | 0 | 1

## Transformer Controls
Branch
From Number | From Name | To Number | To Name | Circuit | Type | Status | Tap Ratio | Phase (Deg) | Automatic Control | Reg Bus Num | Reg Value | Reg Error | Reg Min | Reg Max | Tap Min | Tap Max | Step Size | Reg Bus Name
2 | Left | 1 | 1_TransmissionBus | 1 | LTC | Closed | 1.05 | 0 | NO | 1 | 1 | 0 | 0.99 | 1.01 | 0.9 | 1.1 | 0.00625 | 1_TransmissionBus
3 | Right | 1 | 1_TransmissionBus | 1 | LTC | Closed | 1.05 | 0 | NO | 1 | 1 | 0 | 0.99 | 1.01 | 0.9 | 1.1 | 0.00625 | 1_TransmissionBus

## Switched Shunts
Shunt
Number of Bus | Name of Bus | ID | Reg Bus Num | Status | Status Branch | Control Mode | Auto Control | Regulates | Actual Mvar | Volt High | Volt Low | Reg Volt | Deviation | Nominal Mvar | Max Mvar | Min Mvar | Range Mvar | Percent Mvar
5 | 5ind | 1 | 5 | Closed |  | Fixed | YES | Volt | 1.1 | 1 | 0.99 | 1.048 | 0.048 | 1 | 1 | 0 | 1 | 100
7 | 7res | 1 | 7 | Closed |  | Fixed | YES | Volt | 1.1 | 1 | 0.99 | 1.0477 | 0.0477 | 1 | 1 | 0 | 1 | 100
8 | 8ind | 1 | 8 | Closed |  | Fixed | YES | Volt | 1.1 | 1 | 0.99 | 1.0479 | 0.0479 | 1 | 1 | 0 | 1 | 100
10 | 10res | 1 | 10 | Closed |  | Fixed | YES | Volt | 1.1 | 1 | 0.99 | 1.049 | 0.049 | 1 | 1 | 0 | 1 | 100
12 | 12res | 1 | 12 | Closed |  | Fixed | YES | Volt | 1.1 | 1 | 0.99 | 1.0483 | 0.0483 | 1 | 1 | 0 | 1 | 100
13 | 13ind | 1 | 13 | Closed |  | Fixed | YES | Volt | 1.1 | 1 | 0.99 | 1.0481 | 0.0481 | 1 | 1 | 0 | 1 | 100

## Mismatches
Bus
Number | Name | Area Name | Type | Mismatch MW | Mismatch Mvar | Mismatch MVA
9 | 9com | Commercial | PQ | 0 | 0 | 0
3 | Right | Residential | PQ | 0 | 0 | 0
13 | 13ind | Industrial | PQ | 0 | 0 | 0
10 | 10res | Residential | PQ | 0 | 0 | 0
11 | 11res | Residential | PQ | 0 | 0 | 0
8 | 8ind | Industrial | PQ | 0 | 0 | 0
12 | 12res | Residential | PQ | 0 | 0 | 0
6 | 6com | Commercial | PQ | 0 | 0 | 0
7 | 7res | Residential | PQ | 0 | 0 | 0
5 | 5ind | Industrial | PQ | 0 | 0 | 0
4 | 4com | Commercial | PQ | 0 | 0 | 0
2 | Left | Residential | PQ | 0 | 0 | 0
1 | 1_TransmissionBus | Residential | Slack | 0 | 0 | 0

## Loads
Load
Number of Bus | Name of Bus | Area Name of Load | Zone Name of Load | ID | Status | MW | Mvar | MVA | S MW | S Mvar | Dist Status | Dist MW Input | Dist Mvar Input
4 | 4com | Commercial | Residential | 1 | Closed | 1 | 0.4 | 1.08 | 1 | 0.4 | Closed | 0 | 0
5 | 5ind | Industrial | Residential | 1 | Closed | 1 | 0.6 | 1.17 | 1 | 0.6 | Closed | 0 | 0
6 | 6com | Commercial | Residential | 1 | Closed | 1 | 0.5 | 1.12 | 1 | 0.5 | Closed | 0 | 0
7 | 7res | Residential | Residential | 1 | Closed | 1 | 0.3 | 1.04 | 1 | 0.3 | Closed | 0 | 0
8 | 8ind | Industrial | Residential | 1 | Closed | 1 | 0.6 | 1.17 | 1 | 0.6 | Closed | 0 | 0
9 | 9com | Commercial | Residential | 1 | Closed | 1 | 0.5 | 1.12 | 1 | 0.5 | Closed | 0 | 0
10 | 10res | Residential | Residential | 1 | Closed | 1 | 0.3 | 1.04 | 1 | 0.3 | Closed | 0 | 0
11 | 11res | Residential | Residential | 1 | Closed | 1 | 0.3 | 1.04 | 1 | 0.3 | Closed | 0 | 0
12 | 12res | Residential | Residential | 1 | Closed | 1 | 0.3 | 1.04 | 1 | 0.3 | Closed | 0 | 0
13 | 13ind | Industrial | Residential | 1 | Closed | 1 | 0.6 | 1.17 | 1 | 0.6 | Closed | 0 | 0

## Generators
Gen
Number of Bus | Name of Bus | ID | Status | Gen MW | Gen Mvar | Min MW | Max MW | AGC | AVR | RegBus Num | Set Volt | Min Mvar | Max Mvar | Enforce MW Limits | Part. Factor | Cost Model
1 | 1_TransmissionBus | 1 | Closed | 10.16 | -1.55 | 0 | 1000 | YES | YES | 1 | 1 | -9900 | 9900 | YES | 10 | Cubic

## Buses
Bus
Number | Name | Area Name | Nom kV | PU Volt | Volt (kV) | Angle (Deg) | Gen MW | Gen Mvar | Load MW | Load Mvar | Dist MW | Dist Mvar | Switched Shunts Mvar | Act G Shunt MW | Act B Shunt Mvar | Area Num | Zone Num
1 | 1_TransmissionBus | Residential | 138 | 1 | 138 | 0 | 10.16 | -1.55 | [5 empty] | 0 | 0 | 1 | 1
2 | Left | Residential | 13.8 | 1.0521 | 14.518 | -2.37 | [7 empty] | 0 | 0 | 1 | 1
3 | Right | Residential | 13.8 | 1.0521 | 14.518 | -2.37 | [7 empty] | 0 | 0 | 1 | 1
4 | 4com | Commercial | 13.8 | 1.0492 | 14.478 | -2.94 |  |  | 1 | 0.4 | 0 | 0 |  | 0 | 0 | 2 | 1
5 | 5ind | Industrial | 13.8 | 1.048 | 14.463 | -3.42 |  |  | 1 | 0.6 | 0 | 0 | 1.1 | 0 | 0 | 3 | 1
6 | 6com | Commercial | 13.8 | 1.0469 | 14.447 | -3.78 |  |  | 1 | 0.5 | 0 | 0 |  | 0 | 0 | 2 | 1
7 | 7res | Residential | 13.8 | 1.0477 | 14.459 | -4.06 |  |  | 1 | 0.3 | 0 | 0 | 1.1 | 0 | 0 | 1 | 1
8 | 8ind | Industrial | 13.8 | 1.0479 | 14.462 | -4.19 |  |  | 1 | 0.6 | 0 | 0 | 1.1 | 0 | 0 | 3 | 1
9 | 9com | Commercial | 13.8 | 1.0495 | 14.484 | -2.95 |  |  | 1 | 0.5 | 0 | 0 |  | 0 | 0 | 2 | 1
10 | 10res | Residential | 13.8 | 1.049 | 14.476 | -3.45 |  |  | 1 | 0.3 | 0 | 0 | 1.1 | 0 | 0 | 1 | 1
11 | 11res | Residential | 13.8 | 1.0479 | 14.461 | -3.8 |  |  | 1 | 0.3 | 0 | 0 |  | 0 | 0 | 1 | 1
12 | 12res | Residential | 13.8 | 1.0483 | 14.467 | -4.07 |  |  | 1 | 0.3 | 0 | 0 | 1.1 | 0 | 0 | 1 | 1
13 | 13ind | Industrial | 13.8 | 1.0481 | 14.464 | -4.2 |  |  | 1 | 0.6 | 0 | 0 | 1.1 | 0 | 0 | 3 | 1

## Branches - State
Branch
From Number | From Name | To Number | To Name | Circuit | Status | Branch Device Type | Xfrmr | MW From | Mvar From | MVA From | Lim MVA | % of MVA Limit (Max) | MW Loss | Mvar Loss
2 | Left | 1 | 1_TransmissionBus | 1 | Closed | Transformer | YES | -5.1 | 1 | 5.1 | 12 | 42.9 | 0.03 | 0.21
2 | Left | 3 | Right | 1 | Closed | Line | NO | 0 | -0.1 | 0.1 | 50 | 0.2 | 0 | 0
2 | Left | 4 | 4com | 1 | Closed | Line | NO | 5.1 | -0.9 | 5.1 | 12.7 | 40.4 | 0.02 | 0.05
3 | Right | 1 | 1_TransmissionBus | 1 | Closed | Transformer | YES | -5.1 | 1 | 5.1 | 12 | 42.9 | 0.03 | 0.21
3 | Right | 9 | 9com | 1 | Closed | Line | NO | 5.1 | -1.1 | 5.2 | 12.7 | 40.7 | 0.02 | 0.05
4 | 4com | 5 | 5ind | 1 | Closed | Line | NO | 4 | -1.3 | 4.2 | 12.7 | 33.4 | 0.02 | 0.03
5 | 5ind | 6 | 6com | 1 | Closed | Line | NO | 3 | -0.9 | 3.1 | 12.7 | 24.7 | 0.01 | 0.02
6 | 6com | 7 | 7res | 1 | Closed | Line | NO | 2 | -1.4 | 2.4 | 12.7 | 19.2 | 0.01 | 0.01
7 | 7res | 8 | 8ind | 1 | Closed | Line | NO | 1 | -0.6 | 1.2 | 12.7 | 9.2 | 0 | 0
8 | 8ind | 13 | 13ind | 1 | Closed | Line | NO | 0 | -0.1 | 0.1 | 12.7 | 0.8 | 0 | 0
9 | 9com | 10 | 10res | 1 | Closed | Line | NO | 4 | -1.6 | 4.4 | 12.7 | 34.3 | 0.02 | 0.03
10 | 10res | 11 | 11res | 1 | Closed | Line | NO | 3 | -0.9 | 3.1 | 12.7 | 24.7 | 0.01 | 0.02
11 | 11res | 12 | 12res | 1 | Closed | Line | NO | 2 | -1.2 | 2.3 | 12.7 | 18.4 | 0 | 0.01
13 | 13ind | 12 | 12res | 1 | Closed | Line | NO | -1 | 0.4 | 1.1 | 12.7 | 8.5 | 0 | 0

## Branches - Input
Branch
From Number | From Name | To Number | To Name | Circuit | Status | Branch Device Type | Xfrmr | R | X | B | Lim MVA A | Lim MVA B | Lim MVA C
2 | Left | 1 | 1_TransmissionBus | 1 | Closed | Transformer | YES | 0.1 | 0.8 | 0 | 12 | 12 | 12
2 | Left | 3 | Right | 1 | Closed | Line | NO | 0 | 0.01 | 0 | 50 | 0 | 0
2 | Left | 4 | 4com | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
3 | Right | 1 | 1_TransmissionBus | 1 | Closed | Transformer | YES | 0.1 | 0.8 | 0 | 12 | 12 | 12
3 | Right | 9 | 9com | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
4 | 4com | 5 | 5ind | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
5 | 5ind | 6 | 6com | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
6 | 6com | 7 | 7res | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
7 | 7res | 8 | 8ind | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
8 | 8ind | 13 | 13ind | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
9 | 9com | 10 | 10res | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
10 | 10res | 11 | 11res | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
11 | 11res | 12 | 12res | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
13 | 13ind | 12 | 12res | 1 | Closed | Line | NO | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7

## Branch - Transformer
Branch
From Number | From Name | To Number | To Name | Circuit | Branch Device Type | R | X | B | Lim MVA A | Lim MVA B | Lim MVA C
2 | Left | 1 | 1_TransmissionBus | 1 | Transformer | 0.1 | 0.8 | 0 | 12 | 12 | 12
3 | Right | 1 | 1_TransmissionBus | 1 | Transformer | 0.1 | 0.8 | 0 | 12 | 12 | 12

## Branch - Line
Branch
From Number | From Name | To Number | To Name | Circuit | Branch Device Type | R | X | B | Lim MVA A | Lim MVA B | Lim MVA C
2 | Left | 3 | Right | 1 | Line | 0 | 0.01 | 0 | 50 | 0 | 0
2 | Left | 4 | 4com | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
3 | Right | 9 | 9com | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
4 | 4com | 5 | 5ind | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
5 | 5ind | 6 | 6com | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
6 | 6com | 7 | 7res | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
7 | 7res | 8 | 8ind | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
8 | 8ind | 13 | 13ind | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
9 | 9com | 10 | 10res | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
10 | 10res | 11 | 11res | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
11 | 11res | 12 | 12res | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7
13 | 13ind | 12 | 12res | 1 | Line | 0.0964 | 0.1995 | 0 | 12.7 | 12.7 | 12.7

## Branch - AC and DC
FirstNumber | FirstName | SecondNumber | SecondName | Circuit | Status | Branch Device Type | MW at First Bus | Mvar at First Bus | MVA at First Bus | MW at Second Bus | Mvar at Second Bus | MVA at Second Bus
2 | Left | 1 | 1_TransmissionBus | 1 | Closed | Transformer | -5.1 | 1 | 5.1 | 5.1 | -0.8 | 5.1
3 | Right | 1 | 1_TransmissionBus | 1 | Closed | Transformer | -5.1 | 1 | 5.1 | 5.1 | -0.8 | 5.1
2 | Left | 3 | Right | 1 | Closed | Line | 0 | -0.1 | 0.1 | 0 | 0.1 | 0.1
2 | Left | 4 | 4com | 1 | Closed | Line | 5.1 | -0.9 | 5.1 | -5 | 0.9 | 5.1
3 | Right | 9 | 9com | 1 | Closed | Line | 5.1 | -1.1 | 5.2 | -5 | 1.1 | 5.2
4 | 4com | 5 | 5ind | 1 | Closed | Line | 4 | -1.3 | 4.2 | -4 | 1.4 | 4.2
5 | 5ind | 6 | 6com | 1 | Closed | Line | 3 | -0.9 | 3.1 | -3 | 0.9 | 3.1
6 | 6com | 7 | 7res | 1 | Closed | Line | 2 | -1.4 | 2.4 | -2 | 1.4 | 2.4
7 | 7res | 8 | 8ind | 1 | Closed | Line | 1 | -0.6 | 1.2 | -1 | 0.6 | 1.2
8 | 8ind | 13 | 13ind | 1 | Closed | Line | 0 | -0.1 | 0.1 | 0 | 0.1 | 0.1
9 | 9com | 10 | 10res | 1 | Closed | Line | 4 | -1.6 | 4.4 | -4 | 1.7 | 4.3
10 | 10res | 11 | 11res | 1 | Closed | Line | 3 | -0.9 | 3.1 | -3 | 0.9 | 3.1
11 | 11res | 12 | 12res | 1 | Closed | Line | 2 | -1.2 | 2.3 | -2 | 1.2 | 2.3
13 | 13ind | 12 | 12res | 1 | Closed | Line | -1 | 0.4 | 1.1 | 1 | -0.4 | 1.1